## Overview
Tool for optimizing and simulating off- and on-grid electrification solutions
Excel template for input data and simulation settings
This excel-template serves as an input for an oemof-based optimization and simulation tool. The tool has following features:
* Simulation and evaluation based on electrificy flows, with hourly time-resolution
* Easy adaptation of settings and input parameters
* Easy case definition
* Possibility to perform batch analysis of different locations
* Sensitivity analysis of parameters
* Output: Performance and feasibility indicators, energy flows as csv and as png
| Tab | Function
| settings | Simulation settings
| input_constant | Constant input parameters (Definition of base case for sensitivity analysis)
| input_sensitivity | Input parameters subject to the sensitivity analysis
| project_sites | Input data specific to locations
| case_definitions | Case definitions
| data_sufficiency_check | Check whether data provided in this template is complete

## settings
Defining settings
| General | Electricity solution settings
| Simulated cases | Cases evaluated
| Oemof settings | Oemof-internal simulation settings
| File settings | File locations
| Output – Files | Data saved to file
| Output – Terminal display | Data is displayed in terminal
| Output – Evaluated values | Simulation/evaluation values added to the result file
| setting_name | setting_value
General
| restore_oemof_if_existant | False
| restore_blackouts_if_existant | False
| allow_shortage | True
| evaluated_days | 7
| time_start | 2018-01-01
| time_frequency | H | currently only hourly timestep
| sensitivity_all_combinations | True | If TRUE: All possible combinations of sensitivity parameters are analysed. Results in a huge number of experiments, but enables indentifyin interdependencies
Oemof settings
| solver | cbc
| solver_verbose | False
| cmdline_option | ratioGap | ratioGap, mipgap, AllowedGap
| cmdline_option_value | 0.03
File settings
| output_folder | ./simulation_results
| output_file | results
Output – files
| save_lp_file | False
| lp_file_for_only_3_timesteps | False | This will perform whole simulation with only 3 timesteps!
| save_oemofresults | True
| save_to_csv_flows_storage | False
| save_to_csv_flows_electricity_mg | True
| save_to_png_flows_storage | False
| save_to_png_flows_electricity_mg | True
Output – Terminal display
| display_meta | False
| display_main | False
| display_experiment | False
Output – Evaluated values
| results_demand_characteristics | True
| results_blackout_characteristics | True
| results_annuities | False
| results_costs | False

## input_constant
Definition of constant input parameters
Doubled values | Make sure that the sensitivity setting fits the experiments you want to simulate – either sensitivity or project site values may be preffered
Missing values | Tab “data_sufficiency_check” helps to identify missing /doubled data, but is by no means a thourough check. Python error messages will occur if values are left undefined
Parameter | Value | Unit
blackout_duration | 0 | hrs
blackout_duration_std_deviation | 0 | factor
blackout_frequency | 0 | /mth
blackout_frequency_std_deviation | 0 | factor
combustion_value_fuel | 8.8 | kWh/l
demand_scaling_factor | 1 | factor
distribution_grid_cost_investment | 0 | currency
distribution_grid_cost_opex | 0 | /a
distribution_grid_lifetime | 20 | a
genset_batch | 0.5 | kW
genset_cost_investment | 650 | /kW | using capex of eu islands input parameters
genset_cost_opex | 0 | /kW/a | per kW/a, not operating hours
genset_cost_var | 0 | /kWh
genset_efficiency | 0.33 | factor | not info from sheet
genset_lifetime | 20 | a
genset_max_loading | 1 | factor
genset_min_loading | 0.15 | factor
genset_oversize_factor | 1.2 | factor | (only used if estimated through case definition “peak demand”)
maingrid_distance | 0 | km
maingrid_electricity_price | 0.15 | /kWh
maingrid_extension_cost_investment | 0 | /km
maingrid_extension_cost_opex | 0 | /km/a
maingrid_extension_lifetime | 20 | /km/a
maingrid_feedin_tariff | 0 | /kWh
maingrid_renewable_share | 0 | factor
min_renewable_share | 0 | factor
pcc_oversize_factor | 1.05 | factor | (only used if estimated through case definition “peak demand”)
pcoupling_batch | 1 | kW
pcoupling_cost_investment | 0 | /kW
pcoupling_cost_opex | 0 | /kW/a
pcoupling_cost_var | 0 | /kWh
pcoupling_efficiency | 0.95 | factor
pcoupling_lifetime | 20 | a
price_fuel | 0.89 | /l
project_cost_fix | 0 | currency
project_cost_opex | 0 | /a
project_life | 20 | a
pv_batch | 0.5 | kWp
pv_cost_investment | 1000 | /kWp
pv_cost_opex | 0 | /kWp/a
pv_cost_var | 0 | /kWh
pv_lifetime | 20 | a
shortage_max_allowed | 0 | factor
shortage_penalty_costs | 0.1 | /kWh
stability_limit | 0.4 | factor
storage_batch | 1 | kWh
storage_capacity_max | 1 | factor
storage_capacity_min | 0.2 | factor | Max DOD 80%
storage_cost_investment | 600 | /kWh
storage_cost_opex | 0 | /kWh/a
storage_cost_var | 0 | a
storage_Crate_charge | 1 | factor
storage_Crate_discharge | 1 | factor
storage_inflow_efficiency | 0.9 | factor
storage_initial_soc | None | None or factor
storage_lifetime | 15 | a
storage_loss_timestep | 0 | factor
storage_outflow_efficiency | 1 | factor
tax | 0 | factor
wacc | 0.09 | factor
white_noise_demand | 0 | factor
white_noise_pv | 0 | factor
white_noise_wind | 0 | factor
wind_batch | 0.5 | kW
wind_cost_investment | 1100 | /kW
wind_cost_opex | 0 | /kW/a
wind_cost_var | 0 | /kWh
wind_lifetime | 20 | a

## input_sensitivity
Definition of sensitivity parameters
Deleting rows | Rows can be deleted. Remember to check if the deleted value is defined in input_constant or project_sites
Doubled values | Make sure that the sensitivity setting fits the experiments you want to simulate – either sensitivity or project site values may be preffered
Parameter | Parameter from input_costant that is subject to sensitivity analysis
Min | Minimal value of parameter
Max | Maximal value of parameter
Step | Step lenght for values between min and max value of parameter
Parameter | Min | Max | Step
shortage_max_allowed | 0 | 0.1 | 0.025
genset_lifetime | 10 | 20 | 5

## project_sites
Definition of project locations
Number of locations | An unlimited number of locations can be added below. Make sure that project site names are only used once
Necessary entries | For each project location: project_site_name, timeseries_file, title_time, title_demand, title_pv, title_wind, title_grid_availability, seperator
Additional columns | Project site specific can be defined in additional columns. If one project has a specific value, the value needs to be defined here for all project sites
timeseries_file | The timeseries have to be provided in an external csv file.
title_time | Title of column with timestamp or None
title_demand | Title of column with demand in kW
title_pv | Title of column with PV generation in kW/kWp, or None
title_wind | Title of column with wind generation in kW/kW, or None
title_grid_availability | Title of column with grid availability (boolean) or None
seperator | Seperator used in csv file
project_site_name | timeseries_file | title_time | title_demand | title_pv | title_wind | title_grid_availability | seperator | price_fuel
17_Polo | ./inputs/timeseries/17_Polo.csv | None | Demand | SolarGen | Wind | None | ; | 0.5
34_Araceli | ./inputs/timeseries/34_Araceli.csv | None | Demand | SolarGen | Wind | None | ; | 0.6
107_Balut Is. | ./inputs/timeseries/107_Balut Is..csv | None | Demand | SolarGen | Wind | None | ; | 0.7
126_Pangutaran | ./inputs/timeseries/126_Pangutaran.csv | None | Demand | SolarGen | Wind | None | ; | 0.8

## case_definitions
Case definitions
Adding cases | An unlimited number of cases can be added in new columns. Make sure each has an unique name.
case_name | string
based_on_case | False or True
pv_fixed_capacity | oem, string (name of base capacity case), None
storage_fixed_capacity | oem, string (name of base capacity case), None
genset_fixed_capacity | oem, string (name of base capacity case), None
pcc_consumption_fixed_capacity | oem, string (name of base capacity case), None
pcc_feedin_fixed_capacity | oem, string (name of base capacity case), None
allow_shortage | True or False or default
max_shortage | value
stability_constraint | False or share_usage or share_backup
renewable_constraint | True or False or default
case_name | mg_hybrid_no_min | mg_hybrid | solar_battery_mg | diesel_mg
perform_simulation | False | True | False | False
based_on_case | False | False | False | False
capacity_pv_kWp | oem | oem | oem | None
capacity_storage_kWh | oem | oem | oem | None
capacity_genset_kW | oem | peak_demand | None | peak_demand
genset_with_minimal_loading | False | True | False | True
number_of_equal_generators | 1 | 2 | 1 | 2
capacity_pcc_consumption_kW | None | None | None | None
capacity_pcc_feedin_kW | None | None | None | None
capacity_wind_kW | None | None | None | None
allow_shortage | True | True | True | True
max_shortage | default | default | default | default
stability_constraint | share_hybrid | share_hybrid | share_hybrid | share_hybrid
renewable_constraint | False | False | False | False

## data_sufficiency_check
Data Sufficiency Check
This sheet checks whether the input data set is complete.
| OK | Data set is most likely complete. However, some settings might require multiple definitions (eg. sensitivity analysis with base case). Make sure that values are assigned to parameter mentions!
| 2 | If number of mentions >= 1 Check after simulation, whether parameters were applied properly
| missing! | Missing data!
Parameter name | Sufficient | Number of mentions | Slide
|  |  | settings | input_constant | input_sensitivity | project_sites | case_definitions
restore_oemof_if_existant | OK | 1 | 1 | 0 | 0 | 0 | 0
restore_blackouts_if_existant | OK | 1 | 1 | 0 | 0 | 0 | 0
base_case_with_min_loading | missing! | 0 | 0 | 0 | 0 | 0 | 0
allow_shortage | OK | 2 | 1 | 0 | 0 | 0 | 1
include_stability_constraint | missing! | 0 | 0 | 0 | 0 | 0 | 0
setting_pcc_utility_owned | missing! | 0 | 0 | 0 | 0 | 0 | 0
evaluated_days | OK | 1 | 1 | 0 | 0 | 0 | 0
time_start | OK | 1 | 1 | 0 | 0 | 0 | 0
time_frequency | OK | 1 | 1 | 0 | 0 | 0 | 0
sensitivity_all_combinations | OK | 1 | 1 | 0 | 0 | 0 | 0
solver | OK | 1 | 1 | 0 | 0 | 0 | 0
solver_verbose | OK | 1 | 1 | 0 | 0 | 0 | 0
cmdline_option | OK | 1 | 1 | 0 | 0 | 0 | 0
cmdline_option_value | OK | 1 | 1 | 0 | 0 | 0 | 0
input_folder | missing! | 0 | 0 | 0 | 0 | 0 | 0
output_folder | OK | 1 | 1 | 0 | 0 | 0 | 0
output_file | OK | 1 | 1 | 0 | 0 | 0 | 0
save_lp_file | OK | 1 | 1 | 0 | 0 | 0 | 0
lp_file_for_only_3_timesteps | missing! | 0 | 0 | 0 | 0 | 0 | 0
save_oemofresults | OK | 1 | 1 | 0 | 0 | 0 | 0
save_to_csv_flows_storage | OK | 1 | 1 | 0 | 0 | 0 | 0
save_to_csv_flows_electricity_mg | OK | 1 | 1 | 0 | 0 | 0 | 0
display_graphs_solar | missing! | 0 | 0 | 0 | 0 | 0 | 0
display_graphs_demand | missing! | 0 | 0 | 0 | 0 | 0 | 0
save_to_png_flows_storage | OK | 1 | 1 | 0 | 0 | 0 | 0
save_to_png_flows_electricity_mg | OK | 1 | 1 | 0 | 0 | 0 | 0
display_meta | OK | 1 | 1 | 0 | 0 | 0 | 0
display_main | OK | 1 | 1 | 0 | 0 | 0 | 0
display_invest | missing! | 0 | 0 | 0 | 0 | 0 | 0
display_experiment | OK | 1 | 1 | 0 | 0 | 0 | 0
results_demand_characteristics | OK | 1 | 1 | 0 | 0 | 0 | 0
results_blackout_characteristics | OK | 1 | 1 | 0 | 0 | 0 | 0
results_annuities | OK | 1 | 1 | 0 | 0 | 0 | 0
results_costs | OK | 1 | 1 | 0 | 0 | 0 | 0
blackout_duration | OK | 1 | 0 | 1 | 0 | 0 | 0
blackout_duration_std_deviation | OK | 1 | 0 | 1 | 0 | 0 | 0
blackout_frequency | OK | 1 | 0 | 1 | 0 | 0 | 0
blackout_frequency_std_deviation | OK | 1 | 0 | 1 | 0 | 0 | 0
combustion_value_fuel | OK | 1 | 0 | 1 | 0 | 0 | 0
costs_var_unsupplied_load | missing! | 0 | 0 | 0 | 0 | 0 | 0
demand_scaling_factor | OK | 1 | 0 | 1 | 0 | 0 | 0
distribution_grid_cost_investment | OK | 1 | 0 | 1 | 0 | 0 | 0
distribution_grid_cost_opex | OK | 1 | 0 | 1 | 0 | 0 | 0
distribution_grid_lifetime | OK | 1 | 0 | 1 | 0 | 0 | 0
genset_batch | OK | 1 | 0 | 1 | 0 | 0 | 0
genset_cost_investment | OK | 1 | 0 | 1 | 0 | 0 | 0
genset_cost_opex | OK | 1 | 0 | 1 | 0 | 0 | 0
genset_cost_var | OK | 1 | 0 | 1 | 0 | 0 | 0
genset_efficiency | OK | 1 | 0 | 1 | 0 | 0 | 0
genset_lifetime | OK | 1 | 0 | 1 | 0 | 0 | 0
genset_max_loading | OK | 1 | 0 | 1 | 0 | 0 | 0
genset_min_loading | OK | 1 | 0 | 1 | 0 | 0 | 0
maingrid_distance | OK | 1 | 0 | 1 | 0 | 0 | 0
maingrid_electricity_price | OK | 1 | 0 | 1 | 0 | 0 | 0
maingrid_extension_cost_investment | OK | 1 | 0 | 1 | 0 | 0 | 0
maingrid_extension_cost_opex | OK | 1 | 0 | 1 | 0 | 0 | 0
maingrid_extension_lifetime | OK | 1 | 0 | 1 | 0 | 0 | 0
maingrid_feedin_tariff | OK | 1 | 0 | 1 | 0 | 0 | 0
maingrid_renewable_share | OK | 1 | 0 | 1 | 0 | 0 | 0
max_share_unsupplied_load | missing! | 0 | 0 | 0 | 0 | 0 | 0
min_renewable_share | OK | 1 | 0 | 1 | 0 | 0 | 0
pcoupling_batch | OK | 1 | 0 | 1 | 0 | 0 | 0
pcoupling_cost_investment | OK | 1 | 0 | 1 | 0 | 0 | 0
pcoupling_cost_opex | OK | 1 | 0 | 1 | 0 | 0 | 0
pcoupling_cost_var | OK | 1 | 0 | 1 | 0 | 0 | 0
pcoupling_efficiency | OK | 1 | 0 | 1 | 0 | 0 | 0
pcoupling_lifetime | OK | 1 | 0 | 1 | 0 | 0 | 0
price_fuel | OK | 2 | 0 | 1 | 0 | 1 | 0
project_cost_fix | OK | 1 | 0 | 1 | 0 | 0 | 0
project_cost_opex | OK | 1 | 0 | 1 | 0 | 0 | 0
project_life | OK | 1 | 0 | 1 | 0 | 0 | 0
pv_batch | OK | 1 | 0 | 1 | 0 | 0 | 0
pv_cost_investment | OK | 1 | 0 | 1 | 0 | 0 | 0
pv_cost_opex | OK | 1 | 0 | 1 | 0 | 0 | 0
pv_cost_var | OK | 1 | 0 | 1 | 0 | 0 | 0
pv_lifetime | OK | 1 | 0 | 1 | 0 | 0 | 0
stability_limit | OK | 1 | 0 | 1 | 0 | 0 | 0
storage_batch | OK | 1 | 0 | 1 | 0 | 0 | 0
storage_capacity_max | OK | 1 | 0 | 1 | 0 | 0 | 0
storage_capacity_min | OK | 1 | 0 | 1 | 0 | 0 | 0
storage_cost_investment | OK | 1 | 0 | 1 | 0 | 0 | 0
storage_cost_opex | OK | 1 | 0 | 1 | 0 | 0 | 0
storage_cost_var | OK | 1 | 0 | 1 | 0 | 0 | 0
storage_Crate_charge | OK | 1 | 0 | 1 | 0 | 0 | 0
storage_Crate_discharge | OK | 1 | 0 | 1 | 0 | 0 | 0
storage_inflow_efficiency | OK | 1 | 0 | 1 | 0 | 0 | 0
storage_initial_soc | OK | 1 | 0 | 1 | 0 | 0 | 0
storage_lifetime | OK | 1 | 0 | 1 | 0 | 0 | 0
storage_loss_timestep | OK | 1 | 0 | 1 | 0 | 0 | 0
storage_outflow_efficiency | OK | 1 | 0 | 1 | 0 | 0 | 0
tax | OK | 1 | 0 | 1 | 0 | 0 | 0
wacc | OK | 1 | 0 | 1 | 0 | 0 | 0
white_noise_demand | OK | 1 | 0 | 1 | 0 | 0 | 0
white_noise_pv | OK | 1 | 0 | 1 | 0 | 0 | 0
white_noise_wind | OK | 1 | 0 | 1 | 0 | 0 | 0
wind_batch | OK | 1 | 0 | 1 | 0 | 0 | 0
wind_cost_investment | OK | 1 | 0 | 1 | 0 | 0 | 0
wind_cost_opex | OK | 1 | 0 | 1 | 0 | 0 | 0
wind_cost_var | OK | 1 | 0 | 1 | 0 | 0 | 0
wind_lifetime | OK | 1 | 0 | 1 | 0 | 0 | 0
project_site_name | OK | 1 | 0 | 0 | 0 | 1 | 0
timeseries_file | OK | 1 | 0 | 0 | 0 | 1 | 0
title_time | OK | 1 | 0 | 0 | 0 | 1 | 0
title_demand | OK | 1 | 0 | 0 | 0 | 1 | 0
title_pv | OK | 1 | 0 | 0 | 0 | 1 | 0
title_wind | OK | 1 | 0 | 0 | 0 | 1 | 0
perform_simulation | OK | 1 |  |  |  |  | 1
based_on_case | OK | 1 |  |  |  |  | 1
capacity_pv_kWp | OK | 1 |  |  |  |  | 1
capacity_storage_kWh | OK | 1 |  |  |  |  | 1
capacity_genset_kW | OK | 1 |  |  |  |  | 1
genset_with_minimal_loading | OK | 1 |  |  |  |  | 1
capacity_pcc_consumption_kW | OK | 1 |  |  |  |  | 1
capacity_pcc_feedin_kW | OK | 1 |  |  |  |  | 1
capacity_wind_kW | OK | 1 |  |  |  |  | 1
allow_shortage | OK | 2 | 1 | 0 | 0 | 0 | 1
max_shortage | OK | 1 | 0 | 0 | 0 | 0 | 1
stability_constraint | OK | 1 | 0 | 0 | 0 | 0 | 1
renewable_constraint | OK | 1 | 0 | 0 | 0 | 0 | 1